## Slide 1: Substation Earthing
Mr. Ertuğrul PARTAL
MEng, BEng(Hons), CEng,, MIET
Earthing Systems Consultant and Expert
TESTING & ASSESSMENT
Cigre WG B3.54 Meeting
12-13 March 2019
Graz- Austria

## Slide 2: TEİAŞ(Turkish Electricity Transmission Company)
Notes: SLD dated 28-12-2018
Population: 82 Million(2018)
Area: 814.576 km^2
TEİAŞ has 22 Regional Directorates

## Slide 3: Transmission Lines & Substations owned by TEİAŞ
* 110 subs @ 400 kV
* 1 sub @ 220 kV
* 627 subs @ 154 kV
* 5 subs @ 66 kV
* Total Number of subs: 743
Above substations are owned by TEİAŞ
Transmission Line data |  |  |  |  |  |  |  |  |  |  |  |  | 
 | OVERHEAD LINE |  |  |  |  | UGC |  | SUB-SEA CABLES | TOTAL LENGTH | Total Number of Towers |  |  | 
Regional Directorate | 66 kV | 220 kV | 154 kV | 400 kV | Total Length of OHL | 154 kV | 400 kV | 400 kV |  | 66 kV | 220 kV | 154 kV | 400 kV
1 |  |  | 722,09 | 522,72 | 1244,81 | 164,99 | 47,27 |  | 1457,08 |  |  | 1443 | 935
2 |  |  | 3091,49 | 1155,17 | 4246,66 | 10,18 | 1,66 | 15,96 | 4274,46 |  |  | 6721 | 2361
3 |  |  | 1998,38 | 965,99 | 2964,37 | 38,62 |  |  | 3002,99 |  |  | 4254 | 1924
4 |  |  | 471,41 | 503,40 | 974,81 | 106,51 | 24,78 |  | 1106,11 |  |  | 786 | 1076
5 | 31,34 |  | 1741,74 | 1825,19 | 3598,27 | 2,23 |  |  | 3600,50 | 30 |  | 3523 | 3793
6 |  |  | 1777,01 | 489,14 | 2266,15 |  |  |  | 2266,15 |  |  | 4030 | 1284
7 | 4,11 |  | 1397,69 | 260,47 | 1662,27 |  |  |  | 1662,27 | 17 |  | 3749 | 656
8 |  |  | 1732,74 | 2201,61 | 3934,35 | 42,38 |  |  | 3976,73 |  |  | 3274 | 4981
9 | 32,54 |  | 2313,01 | 881,76 | 3227,32 | 2,95 |  |  | 3230,27 | 156 |  | 5650 | 2083
10 |  |  | 2658,43 | 1499,76 | 4158,19 |  |  |  | 4158,19 |  |  | 6059 | 3363
11 |  |  | 2788,60 | 2309,59 | 5098,19 | 15,37 |  |  | 5113,55 |  |  | 6948 | 6104
12 |  |  | 3015,15 | 1558,33 | 4573,48 | 2,27 |  |  | 4575,75 |  |  | 6634 | 3838
13 |  |  | 2519,72 | 1542,99 | 4062,71 |  |  |  | 4062,71 |  |  | 6573 | 3920
14 |  | 15,73 | 2288,05 | 658,91 | 2962,69 |  |  |  | 2962,69 |  | 45 | 3871 | 1268
15 |  | 69,09 | 1961,36 | 825,00 | 2855,45 | 0,23 |  |  | 2855,68 |  | 196 | 5057 | 2018
16 |  |  | 2293,15 | 1144,88 | 3438,03 |  |  |  | 3438,03 |  |  | 5459 | 2548
17 |  |  | 1755,52 | 791,66 | 2547,17 |  |  |  | 2547,17 |  |  | 4870 | 1999
18 | 39,00 |  | 3837,12 | 1297,45 | 5173,57 | 3,57 |  |  | 5177,14 | 95 |  | 6686 | 2959
19 | 2,68 |  | 1708,77 | 509,66 | 2221,12 | 0,49 |  |  | 2221,61 | 13 |  | 3132 | 903
20 |  |  | 1271,72 | 977,42 | 2249,14 | 1,33 |  |  | 2250,47 |  |  | 3514 | 1981
21 |  |  | 2023,15 | 745,97 | 2769,12 |  |  |  | 2769,12 |  |  | 4676 | 1712
22 |  |  | 1003,04 | 492,09 | 1495,13 |  |  |  | 1495,13 |  |  | 2649 | 1088
TOTAL | 109,67 | 84,82 | 44369,34 | 23159,16 | 67722,99 | 391,12 | 73,72 | 15,96 | 68203,79 | 311 | 241 | 99558 | 52794
 | TOTAL OHL LENGTH |  |  |  | TOTAL UGC LENGTH |  |  | TOTAL SUBSEA CABLE LENGTH |  |  |  |  | 
 | 67.722,99 |  | KM |  | 464,84 | KM |  | 15,96 | KM |  |  |  | 
 |  |  | TOTAL OHL, UGC and SUBSEA CABLE LENGTH |  |  |  |  |  | TOTAL NUMBER OF TOWERS |  |  |  | 
 |  |  | 68.203,79 |  |  | KM |  |  | 152.904 |  |  |  | 
Notes: 01.07.2019 data

## Slide 4: During Commissioning: Design Compliance Checks (Current Practice)
IEEE 80(2000) IEEE 80(2013)-Section 4.1
Target isolated substation earthing system impedance value;
1.00 ohm for 154kV subs
0.5 ohm for 400kV subs
Notes: Current Earthing Design specs for TEİAŞ subs:
Igr = 35 kA for 400 kv subs
Igr = 20 kA for 154 kv subs
Fault Duration: 0.5 seconds
Min s/s earthing conductor CSA: 120 mm^2 to be burried at least 0.5 m from surface(frozen soil situation also be considered)
Allowable Touch & Step Voltage: IEEE 80 limits apply
CYMGRID for some projects but mainly spreadsheet used during design phase
Transfer Voltage Calcs during fault not considered at all
Earthing System Impedance(Resistance) Testing which requires the disconnection of all other paths for ‘dead’ subs

## Slide 5: Testing Experience-1
Testing for 400 & 170 kV energised Overhead Lines (Tower Earthing):
Total of 22 testing set purchased
Measurements are being carried since end of 2017
Testing for 400 & 170 kV energised Substations(Substation Earthing):
1 complete testing set purchased
Total of 22 subs tested over 18 months
‘Earthing Condition Assessment’ reports also prepared
‘Computer Analysis’ section to be added into reports once CDEGS tool purchased by TEİAŞ

## Slide 6: Testing Experience-2
CIT(Low Current, Off Frequency)
Notes: Visual Inspection
Continuity(Integrity) Testing
Soil Resistivity Testing by Wenner Method and modelled by CDEGS(RESAP Module)
Earthing System Impedance Testing: Injected Current 5-30 A @ 60 Hz(Low Current, Off power frequency Injection Test), Z = Measured EPR / Test(Injected) Current
During Injection Testing:
Direct Measurement of EPR via FOP
Direct Measurement of Touch, Step & Transfer Voltages
Measurement of Current Distributions(split factor)
Due to layout of the test circuit, errors due to inductive & capacitive coupling could well be unavoidable therefore, the use of computer modelling(by CDEGS) is essential to correct for the interaction between the test circuit and the earthing system under test and the interactions within the test circuit itself.

## Slide 7: Understanding of Testing Practices-1
Notes: Below Ground Continuity Measurements: Measured resistance acceptance criteria of 20 mohm or less
Above Ground Continuity Measurements: Measured resistance acceptance criteria of 50 micro-ohm or less
Soil pH criteria: If a measured soil pH value is 5.5 or more, soil is not considered hostile to copper

## Slide 8: Understanding of Testing Practices-2
??
??
Notes: RHS: 400 kV Umraniye Substation

## Slide 9: Obligations(Compliance)-1
TS EN 50522(Section 8 & 9) ii) TS 13817(Ref: IEEE 81-2012)
Notes: 1. TS EN 50522(Earthing of Power Installations exceeding 1kv AC)-2010
Annex H: Measuring Touch Voltages
Annex L: Measurements for earthing systems--------HEAVY Current Injection(test currents above 50 A)
Annex M: Site inspection & documentation
2. TS EN 61936-1(Power Installations exceeding 1kv AC)-2010
Related sections from 50522(word by word) insereted into Section 10
3. TS 13817-Methods of grounding resistance measuring methods and evaluation of the results in electrical systems(IEEE 81-2012)-2018
Section 12: Transient Impedance Measurements---??

## Slide 10: Obligations(Compliance)-2
According to ‘Electrical Installations Earthing Regulation(2001)’--- Section-2
Appendix- P recommends that;
Earthing System Tests & Measurements to be carried out at intervals*
* Intervals:
Every 2 to 3 years for substations
Every 5 to 6 years for overhead lines

## Slide 11: The ‘A’ Team 

## Slide 12: COMPUTER Analysis TO BE CARRIED OUT
Overall CDEGS Model of a substation:
Each route should contain at least 20 spans
1700V EPR contour plot for s/s to be overlaid onto a map
Zone of Influence(ZoI) to be assessed
Notes: In the near future!

## Slide 13: Recently Established CIGRE WG;
Notes: EP is a Observer Member of WG C4.50
First WG Meeting was held in September,2018(Paris SESSION)
Second WG meeting will be held in April,2019(Japan)

## Slide 14
THANKS
Mr.Ertuğrul PARTAL- BEng(Hons),MEng,CEng,MIET
Technical Advisor(Earthing Systems & IC Studies for Power Transmission Networks)
Observer Member of Cigre SC C4(Turkey), Full Member of Cigre WG B3.54
M: +90 530 562 44 20 | Ph: +90 312 203 83 26
ertugrul.partal@teias.gov.tr